{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["Mixed Air Temp Ctrl"],"not_rendered":{"images":5,"macros":1,"defined_names":1},"read":"whole","date_system":"1900"}

{"sheet":"Mixed Air Temp Ctrl","index":0,"n_rows":102,"n_cols":97,"rows_kept":102,"merged":[[4,4,5,53],[6,4,7,43],[74,65,74,66],[74,67,74,175],[76,65,76,66],[76,67,76,175],[78,65,78,66],[78,67,78,175],[79,67,79,103],[80,65,80,66],[80,67,80,175],[82,65,82,66],[82,67,82,175]]}
[]
[]
[]
[]
[{"$nulls":4},"Ball Room Air Handling Unit 2 Discharge Air Temperature Control Process  "]
{"$rows_empty":35}
[{"$nulls":96},"."]
{"$rows_empty":31}
[{"$nulls":65},"Notes"]
[]
[{"$nulls":65},1,null,"Coordinate address during submittal review the the project specific hardware requirements and network architecture."]
[]
[{"$nulls":65},2,2,"Tune during the Cx process for stable operation under all operating conditions."]
[]
[{"$nulls":65},3,2,"The design intent is that this loop be a proportional only loop.  Thus the integral and derivative gain should be set to 0 unless directed otherwise by the control system designer or commissioning provider during commissioning"]
[]
[{"$nulls":65},4,2,"The recommended set point for this loop is 40°F.  It is only intended to over-ride the discharge temperature control loop during start-up on a cold day to keep the mixed air plenum above freezing while the system stabilizes."]
[]
[{"$nulls":65},5,2,"The design set point for this system is 52°F"]
{"$rows_empty":18}
[null,"© 2017 Faciltiy Dynamics Engineering - All Rights Reserved"]