## Slide 1: Vapor Compression Refrigeration
Leveraging Phase Changes in Saturated Systems to Provide Cooling
David Sellers
Senior Engineer, Facility Dynamics Engineering

## Slide 2: An Air Cooled Vapor Compression Cycle Chiller

## Slide 3: An Air Cooled Vapor Compression Cycle Chiller
Start with a heat exchanger; a.k.a the evaporator

## Slide 4: An Air Cooled Vapor Compression Cycle Chiller
Add the fluid you want to cool on one side of the heat transfer surface
Start with a heat exchanger; a.k.a the evaporator

## Slide 5: An Air Cooled Vapor Compression Cycle Chiller
Refrigerant
  Substance used to absorb heat from the item or area to be cooled
  Vapor compression cycles leverage the latent heat of vaporization of the refrigerant
    Energy that changes the liquid to a vapor
    The evaporator functions as a saturated system
Start with a heat exchanger; a.k.a the evaporator
Add the fluid you want to cool on one side of the heat transfer surface
Place a refrigerant on the other side of the heat transfer surface

## Slide 6: Phase Changes and Saturated Systems

## Slide 7: Phase Changes and Saturated Systems

## Slide 8: Phase Changes and Saturated Systems

## Slide 9: Phase Changes and Saturated Systems

## Slide 10: Phase Changes and Saturated Systems

## Slide 11: Phase Changes and Saturated Systems

## Slide 12: Phase Changes and Saturated Systems
Phase changes absorb a lot of energy
  Melting ice – 144 Btu/lb
  Heating water – 1Btu/lb-°F
  Converting water to steam – 971 Btu/lb
  Superheating steam – 0.5 Btu/lb
(all parameters are at atmospheric pressure)
Notes: Water
Temp Pressure Density Enthalpy Entropy
Liquid Vapor Liquid Vapor Liquid Vapor
°F psia lbm/cu ft lbm/cu ft Btu/lbm Btu/lbm Btu/lbm °R Btu/lbm °R
211.80 14.650 59.833 0.037201 180.12 1151.0 0.31212 1.7580

## Slide 13: Phase Changes and Saturated Systems
At saturation:
  The substance exists in both a liquid and vapor state
  At a constant pressure, the temperature of the substance will not change until:
    It is fully converted to a liquid (removing energy), or
    It is fully converted to a vapor (adding energy)
Notes: Water
Temp Pressure Density Enthalpy Entropy
Liquid Vapor Liquid Vapor Liquid Vapor
°F psia lbm/cu ft lbm/cu ft Btu/lbm Btu/lbm Btu/lbm °R Btu/lbm °R
211.80 14.650 59.833 0.037201 180.12 1151.0 0.31212 1.7580

## Slide 14: Phase Changes and Saturated Systems An Experiment
Heat water in a low pressure boiler
Monitor:
  Water temperature
  Vapor temperature over the water surface
  Power
Plot the results

## Slide 15: Phase Changes and Saturated Systems An Experiment
Monitoring temperature
Liquid sensor
Vapor sensor
Thermocouple

## Slide 16: Phase Changes and Saturated Systems An Experiment
Monitoring power

## Slide 17: Phase Changes and Saturated Systems An Experiment
Monitoring power

## Slide 23: Vapor Compression Refrigeration Machines
An application of saturated system and phase change principles and concepts

## Slide 24
Evaporation
Compression
Condensation
Expansion

## Slide 25: An Air Cooled Vapor Compression Cycle Chiller

## Slide 27: An Air Cooled Vapor Compression Cycle Chiller

## Slide 28
Evaporator
Suction Line
Liquid Line
Liquid Line Solenoid Valve
Hot Gas Line

## Slide 29: Which Pipe is Which
Suction Line
Liquid Line
Hot gas line
Largest, coldest and insulated
Smallest, warm, usually not insulated
Size between suction and liquid line size, hot, typically not insulated

## Slide 30
Evaporator
Filter Dryer (Not shown on diagram)
Service Valves (Not shown on diagram
Service Bypass to Allow Filter Dryer to be Serviced (Not shown on diagram

## Slide 31
Chilled Water Pipes
Liquid Line Solenoid Valve
Liquid Lines
Suction Line

## Slide 32
Evaporator
Compressor
Liquid Line
Hot Gas Line
Suction Line

## Slide 33
Compressor
Compressor
Suction Line
Hot Gas Lines

## Slide 34
Compressor
Suction Line

## Slide 35
Unloaders

## Slide 36
Crank Case Heater

## Slide 37
Crank Case Heater

## Slide 38
Oil Sight Glass

## Slide 39: Hand Pump for Adding Oil

## Slide 40: Vacuum Pump Evacuating the System in Preparation for Charging
Vacuum Pump

## Slide 42
Condenser
Compressor
Receiver

## Slide 43
Condenser

## Slide 44: Failed Condenser Fan

## Slide 48
Condenser
Receiver
Liquid Line Solenoid Valve
Expansion Valve
Evaporator
Compressor

## Slide 49
Liquid Line Solenoid Valve
Expansion Valve
Liquid Lines
Suction Line

## Slide 50: Electronic Expansion Valve Controllers

## Slide 51: A Refrigerant Sight Glass

## Slide 52: Typical Control Switches

## Slide 53: Adding Hot Gas Bypass
Hot Gas Solenoid
Hot Gas Regulator

## Slide 54
Hot Gas Bypass Lines
Hot Gas Solenoid Valve
Service Valve
Hot Gas Regulator

## Slide 55
Hot Gas Connections to the Evaporator

## Slide 56: Let’s Review

## Slide 57: Name the Parts in the Diagram on the Next Slide

## Slide 58
A
B
C
D
E
F
G

## Slide 59: Name the Parts in the Diagram on the Next Slide
Air Cooled Condenser
Reciever
Liquid Line Solenoid Valve
Expansion Valve
Evaporator
Compressor
Hot Gas Solenoid Valve (Right) and Hot Gas Regulator (Left)

## Slide 60: A Water Cooled Centrifugal Chiller

## Slide 61: Same Cycle, Larger, Centrifugal vs. Screw Compressor, Water vs. Air Cooled

## Slide 62: A Typical Water Cooled Vapor Compression Cycle Chiller
Condenser
Evaporator
Metering Orifices
3 Stage Centrifugal Compressor
CW Supply and Return
CHW Supply and Return
Economizer

## Slide 63: Try Your Hand At Identifying the Parts (Answers Follow)

## Slide 64: A Water Cooled Centrifugal Chiller
7 ?
9 ?
8 ?
2 ?
1 ?
6 ?
5 ?
3 ?
4 ?

## Slide 65: A Water Cooled Centrifugal Chiller
Condenser
Evaporator
Economizer
Three Stage Centrifugal Compressor
Motor
Purge Pump
Suction Elbow
Controls
Lubrication System

## Slide 66: Inside the Condenser
Water Box; Marine Head Type
Tube Sheet
Tubes
Temperature Sensor
Baffle Plate

## Slide 67: Inside the Evaporator
Eliminators
Oil Sump and Pump

## Slide 68: Inside the 3 Stage Compressor

## Slide 69
Impeller (One per Stage)
Diffuser (One per Stage)
Inlet Vane Linkage System
Refrigerant Flow Through a Typical Compressor Stage

## Slide 70: Inlet Vanes and Suction Elbow

## Slide 71: Adding Hot Gas Bypass
Condenser
Evaporator
Metering Orifices
CW Supply and Return
CHW Supply and Return
Economizer
Hot Gas Bypass Valve
3 Stage Centrifugal Compressor

## Slide 72
Compressor
Hot gas valve and piping
Traditional condenser
Suction elbow

## Slide 73: Logging a Centrifugal Chiller’s Inlet Vanes and Hot Gas Bypass

## Slide 78: Adding “Free Cooling”
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve (Typical of 2; Open for Free Cooling)
Hot Gas Bypass Valve
3 Stage Centrifugal Compressor

## Slide 79: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Hot Gas Bypass Valve
Compressor locked out
2 Position Valve Opens

## Slide 80: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Hot Gas Bypass Valve
Compressor locked out
2 Position Valve Opens

## Slide 83: A Heat Recovery Centrifugal Chiller
The chiller in the following slide has a second condenser tube bundle that is piped to the heating hot water system. This allows the hot gas off of the compressor to be used to generate hot water for reheat loads prior to having its heat rejected to the cooling tower via the traditional condenser.

## Slide 86
Hot gas valve and piping
Compressor
Evaporator
Traditional condenser
Heat recovery condenser
Suction elbow